ONE GE FRAME 7EA GAS TURBINE GENERATOR SET

 12 September 2003
I.

SCOPE OF  SUPPLY


One complete combustion turbine generator units including GE’s standard equipment as well as special accessories and services detailed below.

The combustion turbine package includes, but is not limited to, the following:

a. Lubricating oil system with water/oil coolers and stainless steel supply oil piping and carbon steel return oil piping common to the combustion turbine and generator.

b. Natural gas valve train and control package.

c. On and off line compressor water wash system.

d. 4,160V AC motor starting system.

e. Hydraulic ratchet rotor turning system arranged for automatic engagement and disengagement complete with a jog switch.

f. Inlet silencer, self-cleaning pulse type filters, ductwork expansion joints & supports.

g. Exhaust flange.

h. Emission control system ‑ Dry Low NOx, (DLN) combustion system.

i. Enclosure with acoustic treatment and barrier walls along the GT exhaust plenum.

j. Control and protection system including provisions for interconnection to Purchaser's DCS system via an RS232C (Modbus).

k. Vibration and temperature instrumentation and monitoring system including a Bentley-Nevada system for interfacing with the Purchaser's DCS.

l. Mark V turbine control system that includes one (1) local and one (1) remote Windows based interface system.

m. Piping on skids supplied by the Seller.

n. Inlet bleed heating system including the inlet duct bleed heat manifold and the GT air extraction piping system.

o. Shop tests.

p. Witness turbine control panel - final check   (already completed as of 15 July 01).

q. Witness turbine panel factory test demonstration (already completed as of 15 July 01).

r. Cleaning and primer painting only.

s. Air intake anti-icing provisions.


One TEWAC non‑salient pole 3,600-rpm generators designed in accordance with the Rating and Operational Requirements specified herein, including, but not limited to, the following:


a. GE 7A6 generator rated at 102.8 MVA, 0.8 pf, 60 Hz and 13.8 kV.

b. Coolers designed with 90-10 copper nickel tubes

c. On base instruments include:  platinum stator RTDs, oil & bearing thermocouples, flux probe and Bentley vibration probes

d. All electrical equipment meets CSA codes.

e. Generator line side equipment located in a skid mounted enclosure complete with generator circuit breaker, draw-out voltage transformers, surge protection and one set of current transformers.

f. Generator neutral grounding equipment located in a skid mounted enclosure complete with four sets of current transformers.

g. Redundant generator protections (GE DGP and Multilin SR-489 relays)

h. Generator control through the Mark V turbine control system includes: auto-synchronizing, metering, isochranous and droop control modes.

i. Space heaters

j. Standard generator accessories as outlined in Seller's apparatus handbook in effect at the time of purchase order award.



A static excitation system, minimum response ratio of 2.0, with adequate capacity for supplying the generator field current requirements specified herein, including, but not limited to, the following:

a. Thysistor excitation system, with controls and protection equipment and cubicles.

b. De‑excitation thyristor.

c. Generator field collector rings.

d. Generator field winding automatic ground detector equipment.

e. Generator field current for remote indication and protective relays.

f. DC regulator and manual generator field voltage adjuster.

g. AC regulator for automatic generator terminal voltage control, static type.

h. Regulator transfer equipment.

i. Remote mounted indicators for generator and exciter field voltages, currents, and DC/AC regulator comparison Voltage through the Mark V.

j. Electrical interconnections with-in skids or enclosures.

k. Interconnecting piping within, skids or enclosures.

l. Control and indication through the Mark V ---Part of the master control panels.

m. Excitation protecting equipment.

n. Standard excitation system accessories as outlined in Seller's apparatus handbook in effect at the time of purchase order award.

o. Power System stabilizer.


Baseplates with above grade sole plates if required

Above grade sole plates for auxiliary skids and other miscellaneous equipment, if required

Turbine‑generator control panel, see attached diagram defining boundaries.

Fire and smoke detection and protection systems for the combustion turbine compartment and auxiliary modules and definition of hazardous area classification.

Installation and start-up, technical advice and direction.


Documentation as agreed at Design Finalization Meeting detailed in the two Schedules of Required Documents.

Start-up and commissioning spares

Miscellaneous electrical equipment:

a. Packaged and pre-wired electrical module that contains:  Mark V and EX2000 cubicles,


b. generator protections, 480 V AC and 125 V DC MCCs, 125 V battery system with chargers

c. Control devices, wiring, and cabinets within skids

d. Terminal boxes, conduit, and fittings within skids

e. Lighting and convenience outlets within control panels and enclosures



                                                                                                                                    2 of 3

